## Cover
ZENITH MECHANICAL SERVICES
Plumbing & Gas Services
82 Viewpoint Business Centre, Consett, County Durham, DH8 6BN
Contact Number: 01207 693 849
Email: admin@zenithmechanical.com
REPORT ON
Whinstone Lodge
NE25 8DB
CARRIED OUT ON BEHALF OF
S4NT
REPORT NUMBER: 22-23902
DATE OF REPORT: 31/10/2022
Registered in England Company No. 923602
Directors: Josh Hodgson and David Hunter |  | Gas Safe registration number: 527432

## Contents
ZENITH MECHANICAL SERVICES
Report Number | 22-23902
Contents of Report
Section 1 | Job information
Section 2 | Introduction
Section 3 | Report
Section 4 | Photographs
SECTION 1: Job Information
Client | S4NT
Address | 21b West Chirton Industrial Estate
Oak Road
West Chirton
North Shields
NE29 8SF
Site Address | Whinstone Lodge
NE25 8DB
Carried Out On | 11/10/2022, 31/10/2022
Survey Completed By | Rob Porritt
SECTION 2: Introduction
No Heating to the whole block

## Report
ZENITH MECHANICAL SERVICES
Report Number | 22-23902
SECTION 3: Report
FOW REQUIRED, REPLACE HEATING 3 PORT ACTUATOR Arrived on site no heating, boilers locked out on overheat. I tested 3 port valve, no flow, removed cover from actuator, water from flue pipe above actuator had ran into PCB housing and damaged actuator motor. Power and bms had shorted. I removed actuator head from body and manually operated flow through 3 port. Reset 2 hamworthy boiler and returned heating water temperature to 70 dc and rising. I also reset water heater 2. If Zenith are to fit new actuator BMS engineer required to test and verify signalling is correct. Returned to site, fitted new actuator, wired new actuator as per photos, actuator NOT working. PLEASE arrange for bms engineer to attend site as previously requested. I HAVE REMOVED ACTUATOR AND MANUALLY OPENED VALVE TO SUPPLY HEATING TO SITE. NEW ACTUATOR IS JN PLANTROOM

## Photos
ZENITH MECHANICAL SERVICES
Report Number | 22-23902
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 22-23902
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 22-23902
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 22-23902
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 22-23902
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes