## Cover
ZENITH MECHANICAL SERVICES
Plumbing & Gas Services
82 Viewpoint Business Centre, Consett, County Durham, DH8 6BN
Contact Number: 01207 693 849
Email: admin@zenithmechanical.com
REPORT ON
Pembroke Court
Hylton Lane
Downhill
SR5 4DF
CARRIED OUT ON BEHALF OF
Karbon Homes
REPORT NUMBER: 22-24007
DATE OF REPORT: 14/10/2022
Registered in England Company No. 923602
Directors: Josh Hodgson and David Hunter |  | Gas Safe registration number: 527432

## Contents
ZENITH MECHANICAL SERVICES
Report Number | 22-24007
Contents of Report
Section 1 | Job information
Section 2 | Introduction
Section 3 | Report
Section 4 | Photographs
SECTION 1: Job Information
Client | Karbon Homes
Address | Number Five
Gosforth Park Avenue
Gosforth Business Park
Newcastle upon Tyne
NE12 8EG
Site Address | Pembroke Court
Hylton Lane
Downhill
SR5 4DF
Carried Out On | 14/10/2022
Survey Completed By | Rob Porritt
SECTION 2: Introduction
Small commercial boiler in bin store that serves the corridor to block 29-40 - --- Heating not working ---- Please repair as necessary ---- ---- Standard Callout for Commerical Boilers

## Report
ZENITH MECHANICAL SERVICES
Report Number | 22-24007
SECTION 3: Report
Boiler off on overheat, inspected boiler and found the following Pump not running, impeller motor failed , boiler spark and flame probes worn and boiler over heat stat not reading correct resistance. Travelled to merchants merchants and back to site Replaced Grunfos Pump, electrodes and overheat stat, tested boiler, pump and radiators, Completed flue gas analysis Readings not safe Investigated boiler, found Burner ceramic broken Leaking HEX Signs of spillage Case seal leaking Quote to fit new boiler

## Photos
ZENITH MECHANICAL SERVICES
Report Number | 22-24007
SECTION 4: Photos
Room / Area
V
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 22-24007
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 22-24007
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 22-24007
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 22-24007
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes