## Cover
ZENITH MECHANICAL SERVICES
Plumbing & Gas Services
82 Viewpoint Business Centre, Consett, County Durham, DH8 6BN
Contact Number: 01207 693 849
Email: admin@zenithmechanical.com
REPORT ON
18 Penine Avenue
Chester-Le-Street
County Durham
DH2 3AU
CARRIED OUT ON BEHALF OF
Karbon Homes
REPORT NUMBER: 22-25290
DATE OF REPORT: 22/11/2022
Registered in England Company No. 923602
Directors: Josh Hodgson and David Hunter |  | Gas Safe registration number: 527432

## Contents
ZENITH MECHANICAL SERVICES
Report Number | 22-25290
Contents of Report
Section 1 | Job information
Section 2 | Introduction
Section 3 | Report
Section 4 | Photographs
SECTION 1: Job Information
Client | Karbon Homes
Address | Number Five
Gosforth Park Avenue
Gosforth Business Park
Newcastle upon Tyne
NE12 8EG
Site Address | 18 Penine Avenue
Chester-Le-Street
County Durham
DH2 3AU
Carried Out On | 22/11/2022, 25/11/2022
Survey Completed By | Rhys Brown
SECTION 2: Introduction
Manifold blocked either requires power flush on system or to locate manifold (possibly under kitchen floor) and unblocked flow that way

## Report
ZENITH MECHANICAL SERVICES
Report Number | 22-25290
SECTION 3: Report
Jw 21-11-22 Baxi duotec 28 House on 10mm copper Need to locate manifold or power flush Run boiler max rate flow is hot but no rads get anything to them even the bypass Living room and bedroom are carpet Kitchen hall and bathroom are Lino that is glued down A would say manifold will be in living room as these property’s all had BBU prior to combi in kitchen RB- 22/11/22 Attended job put boiler in max rate but overheated within seconds leading to me thinking the heat isn’t leaving the boiler, took outer casing off and seen that diverter valve was badly fured up. Took actuator head off and checked if pin was free which it was. Inspected pin inside of head to see that there was no movement when trying to change it from heating to hot water. Picked up head from wolsley team valley under job number and replaced, checked rads and they were heating up. No need for a return visit.

## Photos
ZENITH MECHANICAL SERVICES
Report Number | 22-25290
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 22-25290
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 22-25290
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 22-25290
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 22-25290
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes