## Cover
ZENITH MECHANICAL SERVICES
Plumbing & Gas Services
82 Viewpoint Business Centre, Consett, County Durham, DH8 6BN
Contact Number: 01207 693 849
Email: admin@zenithmechanical.com
REPORT ON
Eccles Grange
Church Road
Backworth
NE27 0FW
CARRIED OUT ON BEHALF OF
S4NT
REPORT NUMBER: 23-33975
DATE OF REPORT: 28/11/2023
Registered in England Company No. 923602
Directors: Josh Hodgson and David Hunter |  | Gas Safe registration number: 527432

## Contents
ZENITH MECHANICAL SERVICES
Report Number | 23-33975
Contents of Report
Section 1 | Job information
Section 2 | Introduction
Section 3 | Report
Section 4 | Photographs
SECTION 1: Job Information
Client | S4NT
Address | Quadrant The Silverlink North
Colbalt Business Park
North Tyneside
NE27 0BY
Site Address | Eccles Grange
Church Road
Backworth
NE27 0FW
Carried Out On | 10/07/2023
Survey Completed By | Graham Parker
SECTION 2: Introduction
6 Monthly PPM / Mechanical Check

## Report
ZENITH MECHANICAL SERVICES
Report Number | 23-33975
SECTION 3: Report
2 x Hamworthy fleet f250v boilers 1= operational 2= Operational 2 x Hamworthy powerstock calorifiers 1= operational 2= operational 1 x mikrofill pressurisation units 1= operationall 2 x DHWS 60 litre expansion vessels 1 =requires replacement 60 litre floor standing 2= operational 1 x LTHW expansion vessel = requires replacement 200 litre floor standing Lagging = good Flue = good Gauges =operational Valves = operational Zone 1 pumps = wilo stratos d40/1-12 pumps 1= operational 0.4 amps 2= operational 0.4 amps Primary pumps = wilo stratos d40/1-12 1= operational 1.5 amps 2 = operational 1.5 amps Air and dirt separator = drained and cleaned out 2 x biral destrat pumps 1 = operational 0.3 amps 2 = operational 0.3 amps Interlock = operational A lot of scale on 28mm secondary hot water pipe work of a leak 1 x secondary return pump wilo stratos pico-z = operational 0.3 amps Condensate pipe work = good Water test = PH8 @ 27 degrees

## Photos
ZENITH MECHANICAL SERVICES
Report Number | 23-33975
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 23-33975
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 23-33975
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 23-33975
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 23-33975
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes