## Cover
ZENITH MECHANICAL SERVICES
Plumbing & Gas Services
82 Viewpoint Business Centre, Consett, County Durham, DH8 6BN
Contact Number: 01207 693 849
Email: admin@zenithmechanical.com
REPORT ON
John Buddle Work Village
Buddle Road
Newcastle Upon Tyne
NE4 8AW
CARRIED OUT ON BEHALF OF
RHWE Ltd
REPORT NUMBER: 23-34207
DATE OF REPORT: 14/11/2023
Registered in England Company No. 923602
Directors: Josh Hodgson and David Hunter |  | Gas Safe registration number: 527432

## Contents
ZENITH MECHANICAL SERVICES
Report Number | 23-34207
Contents of Report
Section 1 | Job information
Section 2 | Introduction
Section 3 | Report
Section 4 | Photographs
SECTION 1: Job Information
Client | RHWE Ltd
Address | RHWE Ltd
John Buddle Work Village
Buddle Road
Newcastle upon Tyne
NE4 8AW
Site Address | John Buddle Work Village
Buddle Road
Newcastle Upon Tyne
NE4 8AW
Carried Out On | 12/07/2023
Survey Completed By | Graham Parker
SECTION 2: Introduction
6 Monthly PPM / Mechanical Check

## Report
ZENITH MECHANICAL SERVICES
Report Number | 23-34207
SECTION 3: Report
BUDDLE HOUSE 1 x ideal Evomax 2 60kw= operational 2 x grundfos UPSD 50-180f vt pumps 1 = operational 3.6 amps 2= operational 3.6 amps 1 x jet pressurisation unit = operational 1 x trend iq220 BMS = operational 1 x Remeha aqua calorifier = operational,no destrat pump fitted Flue = satisfactory Lagging = average No visible leaks PRV,S = good Valves = operational Safety controls = satisfactory 1 x DHWS expansion vessel = operational charged to 3.5 bar 1 x LTHW expansion vessel = operational charged to 1.5 bar Gauges = satisfactory Ventilation vent axia = operational and satisfactory JOHN BUDDLE WORK VILLAGE 1 x ideal Evomax 2 60kw = operational 1 Remeha Quinta 65 = off and isolated due to flue totally corroded through 1 x broag pressurisation unit = off and isolated due to split internal pipe which has sprayed on to the electrical components and also broken unit isolator 2 x grundfos UPSD 50-180 f vt pumps 1 = operational 3.1 amps 2 = operational 3.1 amps 1 x vent axia SLPT ventilation unit = operational Valves = operational Gauges = operational 1 x trend iq 220 BMS = operational 1 x floor standing 110 litre LTHW expansion vessel = operational charged to 1.5 bar 8 x heatrae sadia FBM water heaters including 3 located within workshops 1 to 3 1 = operational no signs of leaks 2 = operational no signs of leaks 3 = operational no signs of leaks 4 = operational no signs of leaks 5 = operational no signs of leaks 6 = operational no signs of leaks 7 = operational no signs of leaks 8 = operational no signs of leaks Flue = satisfactory

## Photos
ZENITH MECHANICAL SERVICES
Report Number | 23-34207
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 23-34207
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 23-34207
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 23-34207
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 23-34207
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes