## Cover
ZENITH MECHANICAL SERVICES
Plumbing & Gas Services
82 Viewpoint Business Centre, Consett, County Durham, DH8 6BN
Contact Number: 01207 693 849
Email: admin@zenithmechanical.com
REPORT ON
Windsor Grange
Windsor Drive
Howdon
NE28 0NP
CARRIED OUT ON BEHALF OF
S4NT
REPORT NUMBER: 23-36878
DATE OF REPORT: 29/01/2024
Registered in England Company No. 923602
Directors: Josh Hodgson and David Hunter |  | Gas Safe registration number: 527432

## Contents
ZENITH MECHANICAL SERVICES
Report Number | 23-36878
Contents of Report
Section 1 | Job information
Section 2 | Introduction
Section 3 | Report
Section 4 | Photographs
SECTION 1: Job Information
Client | S4NT
Address | Quadrant The Silverlink North
Colbalt Business Park
North Tyneside
NE27 0BY
Site Address | Windsor Grange
Windsor Drive
Howdon
NE28 0NP
Carried Out On | 09/11/2023
Survey Completed By | Craig Towart
SECTION 2: Introduction
Mechanical Checks

## Report
ZENITH MECHANICAL SERVICES
Report Number | 23-36878
SECTION 3: Report
Ct 9/11 2x hamworthy fleet f175v 1= operational 2= operational 2x lochinvoir eco shield calorifier 1= operational 2=operational 2x wilo pressuration units 1= operational (service due) 2= operational (service due) 1x C/H expansion vessel operational charged to 1.5bar 1x Ashp expansion vessel operational charged to 1.5bar 2x DHW expansion vessel both operational and charged to 1.9 as vessel states Valves operational Gauges operational expect one on hot water flow showing false temp. Flues good 6x prv all operational 2x temperature release valve operational 1x interlock operational Lagging good Water test awaiting results Heating zone 1 pumps 2x Grundfoss magna 3d 40-100-220 1= operation amps 0.32 2= operational 0.27 amps Heating zone 2 pumps 2x Grundfoss magna 3d 40-150-250 1= operational 0.31 amps 2= operational 0.28 amps ASHP primary pumps 2x wilo tl4 1= operational amps 1.4 2= operational amps 1.2 ASHP secondary 2x Grundfoss magna 3d 32-80-180 1= operational amps 0.09 2= operational amps 0.1 DHW Secondary return pump 1x Grundfoss ups15-50 Operational amps 0.24 2x vt valve Schneider m700-s2-srsd 1=operational 2= operational BMS not showing any temps on screens just yellow triangles. FoW awaiting test results

## Photos
ZENITH MECHANICAL SERVICES
Report Number | 23-36878
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 23-36878
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 23-36878
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 23-36878
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 23-36878
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes