## Cover
ZENITH MECHANICAL SERVICES
Plumbing & Gas Services
82 Viewpoint Business Centre, Consett, County Durham, DH8 6BN
Contact Number: 01207 693 849
Email: admin@zenithmechanical.com
REPORT ON
Whinstone Lodge
Front Street
Whitley Bay
NE25 8DJ
CARRIED OUT ON BEHALF OF
S4NT
REPORT NUMBER: 23-39515
DATE OF REPORT: 29/01/2024
Registered in England Company No. 923602
Directors: Josh Hodgson and David Hunter |  | Gas Safe registration number: 527432

## Contents
ZENITH MECHANICAL SERVICES
Report Number | 23-39515
Contents of Report
Section 1 | Job information
Section 2 | Introduction
Section 3 | Report
Section 4 | Photographs
SECTION 1: Job Information
Client | S4NT
Address | Quadrant The Silverlink North
Colbalt Business Park
North Tyneside
NE27 0BY
Site Address | Whinstone Lodge
Front Street
Whitley Bay
NE25 8DJ
Carried Out On | 23/11/2023
Survey Completed By | Craig Towart
SECTION 2: Introduction
Carry out 6 Month Mechanical Checks

## Report
ZENITH MECHANICAL SERVICES
Report Number | 23-39515
SECTION 3: Report
Ct 23/11 2x hamworthy f85v boilers 1= operational 2= operational 2x lochinvoir eco shield calorifier 1= Off 2= operational 1x vt valve Schneider = operational 1x interlock operational 2x hamworthy chesil Pressuration unit 1= operational 2=operational 1x heating expansion vessel 1.6bat 1x ashp expansion vessel 1.6bar 2xDHW expansion vessel 1= 3bar 2= 3bar Ashp primary pumps 2x groundfoss magna 3 40-80 1=operational amps 0.3 2= operational amps 0.26 Ashp secondary 2x groundfoss magna 3 32-40 1= underperforming damaged screen amps 0.02 2= operational amps 0.09 Heating pumps 2x groundfoss magna 3 40-120 1= operational amps 0.2 2 = internal sensor fault amps 0.24 Dhw secondary return pump groundfoss 1=operational amps 0.1 Prv x6 operational Lagging good Flue good Gauges operational Valves operational Sensors unknown as BMS not showing value Pipe work on Dhw secondary return pump is copper to steel carbon needs brass between

## Photos
ZENITH MECHANICAL SERVICES
Report Number | 23-39515
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 23-39515
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 23-39515
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 23-39515
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 23-39515
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes