## Cover
ZENITH MECHANICAL SERVICES
Plumbing & Gas Services
82 Viewpoint Business Centre, Consett, County Durham, DH8 6BN
Contact Number: 01207 693 849
Email: admin@zenithmechanical.com
REPORT ON
Southgate Court
Camsey Close
Longbenton
NE12 8UW
CARRIED OUT ON BEHALF OF
S4NT
REPORT NUMBER: 23-39518
DATE OF REPORT: 29/01/2024
Registered in England Company No. 923602
Directors: Josh Hodgson and David Hunter |  | Gas Safe registration number: 527432

## Contents
ZENITH MECHANICAL SERVICES
Report Number | 23-39518
Contents of Report
Section 1 | Job information
Section 2 | Introduction
Section 3 | Report
Section 4 | Photographs
SECTION 1: Job Information
Client | S4NT
Address | Quadrant The Silverlink North
Colbalt Business Park
North Tyneside
NE27 0BY
Site Address | Southgate Court
Camsey Close
Longbenton
NE12 8UW
Carried Out On | 21/11/2023
Survey Completed By | Craig Towart
SECTION 2: Introduction
Carry out 6 Month Mechanical Checks

## Report
ZENITH MECHANICAL SERVICES
Report Number | 23-39518
SECTION 3: Report
Ct 21/11 3x hamworthy f150v 1= turned off (awaiting repair) 2= operational 3= operational 2x hamworthy powerstock calorifier 1= operational 2= operational 1x hamworthy chiesl pressuration unit =operational but damaged screen 1x heating expansion vessel = re charged to 1.6bar 2x DHW expansion vessel 1= represuured to 3.5 bar 2= 3.5bar 2x3 port valve Schneider 1=operational 2= operational 2x vt valve Schneider 1=operational 2= operational DHW primary pumps 2x Groundfoss magna 3 32-100 1= operational amps 0.1 2= operational amps 0.1 DHW Secondary return pump 1x groundfoss ups 32-80 operational amps 0.7 Zone1 pumps 2x groundfoss magna 3 40-150 1= operational amps 0.3 2= operational amps 0.28 Zone2 pumps 2x groundfoss magna 3 40-120 1= operational amps 0.18 2= operational amps 0.24 Flue showing one old leak Gauges and sensors operational Valves all operational now replaced broken valve on cal 1 expansion vessel due to been a safety concern not reopening. Prv x8 all operational Lagging good 1x interlock operational BMS not showing any values on screen Materials used 28mm lockable gate valve

## Photos
ZENITH MECHANICAL SERVICES
Report Number | 23-39518
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 23-39518
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 23-39518
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 23-39518
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 23-39518
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes