## Cover
ZENITH MECHANICAL SERVICES
Plumbing & Gas Services
82 Viewpoint Business Centre, Consett, County Durham, DH8 6BN
Contact Number: 01207 693 849
Email: admin@zenithmechanical.com
REPORT ON
Robinson House
Grant Street
Horden
SR8 4DD
CARRIED OUT ON BEHALF OF
Believe Housing
REPORT NUMBER: 23-39521
DATE OF REPORT: 18/12/2023
Registered in England Company No. 923602
Directors: Josh Hodgson and David Hunter |  | Gas Safe registration number: 527432

## Contents
ZENITH MECHANICAL SERVICES
Report Number | 23-39521
Contents of Report
Section 1 | Job information
Section 2 | Introduction
Section 3 | Report
Section 4 | Photographs
SECTION 1: Job Information
Client | Believe Housing
Address | Coast House
Spectrum 4
Spectrum Business Park
Seaham
SR7 7TT
Site Address | Robinson House
Grant Street
Horden
SR8 4DD
Carried Out On | 18/12/2023
Survey Completed By | Craig Towart
SECTION 2: Introduction
Carry out 6 Month Mechanical Checks

## Report
ZENITH MECHANICAL SERVICES
Report Number | 23-39521
SECTION 3: Report
Ct 18/12 2 x de Dietrich boilers 1= operational 2= operational 2 x lochinvar gas water heater 1= operational 2= isolated 1x pressuration unit lowara operational 2x shunt pumps grundfos magna 1d 40-80f 220 1=operational amps 0.28 2 = operational amps0.25 2x district pumps Grundfoss upsd 65-60/4f 1=operational amps 0.2= operational amps 0 .55 2x house pumps Grundfoss ups 65/180 1= operational amps 2= tripped on BMS tried resetting but nothing looks to have tripped and no paper work to see which relay it goes too 1x DHW return pump grundfos ups 15-50 = operational amps 0.23 1x heating expansion vessel charged at 1.5bar 1x potable expansion vessel charged at 3bar Lagging ok Valves and gauges operational Flues good condition 1x interlock operational 1x esbe 3way valve = manual position head already removed. Pictures of motorised head that would need replaced attached. Water sample awaiting results

## Photos
ZENITH MECHANICAL SERVICES
Report Number | 23-39521
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 23-39521
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 23-39521
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 23-39521
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 23-39521
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes