## Cover
ZENITH MECHANICAL SERVICES
Plumbing & Gas Services
82 Viewpoint Business Centre, Consett, County Durham, DH8 6BN
Contact Number: 01207 693 849
Email: admin@zenithmechanical.com
REPORT ON
Moorcroft
Bowman Drive
Dudley
NE23 7FF
CARRIED OUT ON BEHALF OF
S4NT
REPORT NUMBER: 23-41043
DATE OF REPORT: 19/01/2024
Registered in England Company No. 923602
Directors: Josh Hodgson and David Hunter |  | Gas Safe registration number: 527432

## Contents
ZENITH MECHANICAL SERVICES
Report Number | 23-41043
Contents of Report
Section 1 | Job information
Section 2 | Introduction
Section 3 | Report
Section 4 | Photographs
SECTION 1: Job Information
Client | S4NT
Address | Quadrant The Silverlink North
Colbalt Business Park
North Tyneside
NE27 0BY
Site Address | Moorcroft
Bowman Drive
Dudley
NE23 7FF
Carried Out On | 11/01/2024
Survey Completed By | Craig Towart
SECTION 2: Introduction
Carry out 6 Monthly Mechanical Checks in Plantroom.

## Report
ZENITH MECHANICAL SERVICES
Report Number | 23-41043
SECTION 3: Report
Ct 11/1/24 Boilers 3x remeha Quinta pro 1= operational 2= operational 3= operational 2x calorifiers 1= operational 2= operational 2x dhw expansion vessels 1= no pressure pressurised @3.5 seems to be holding pressure now recommend replacing however 35liter 1” connection potable expansion vessel 2= pressurised @ 2bar re pressurised @3.5 1x ch expansion vessel = operational pressurised @1.5 bar 7x prv Flamco pressurisation unit operational 1x interlock operational Primary pumps 1x grundfos Magna 50-120f operational amps 0.4 1x grundfos magna 3 50-120 f operational amps 0.3 Vt pumps 2x geundfos magna 65-120f 1= operational amps 0.4 2= operational amps 0.4 Secondary return pump grundfos Magna 32-100n operational amps 0.2 2x 3 way valves Siemens acvatix ssc61.5 operational 1x vt valve Siemens acvatix sqk84 Gauges operational Valves operational Sensors operational Water sample took Lagging ok Pipework ok few signs of old leaks dried up. (Not worth disturbing with threaded steel pipe) Flue ok sign of leak on joint but dry so may been already repaired Condensate pipe on boilers to be replaced as leaks have corroded through prv pipe. ( materials 3m 1 1/2 solvent pipe 3x 1 1/2 solvent tee 3x 1 1/2 to 3/4 reducers 1x 1 1/2 rodding eye 3x 1 1/2 90s 1x 1 1/2 connectors)

## Photos
ZENITH MECHANICAL SERVICES
Report Number | 23-41043
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 23-41043
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 23-41043
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 23-41043
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 23-41043
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes