## Cover
ZENITH MECHANICAL SERVICES
Plumbing & Gas Services
82 Viewpoint Business Centre, Consett, County Durham, DH8 6BN
Contact Number: 01207 693 849
Email: admin@zenithmechanical.com
REPORT ON
Ferndene
Threap Gardens
Howdon
NE28 7HT
CARRIED OUT ON BEHALF OF
S4NT
REPORT NUMBER: 24-41860
DATE OF REPORT: 30/01/2024
Registered in England Company No. 923602
Directors: Josh Hodgson and David Hunter |  | Gas Safe registration number: 527432

## Contents
ZENITH MECHANICAL SERVICES
Report Number | 24-41860
Contents of Report
Section 1 | Job information
Section 2 | Introduction
Section 3 | Report
Section 4 | Photographs
SECTION 1: Job Information
Client | S4NT
Address | Quadrant The Silverlink North
Colbalt Business Park
North Tyneside
NE27 0BY
Site Address | Ferndene
Threap Gardens
Howdon
NE28 7HT
Carried Out On | 25/01/2024
Survey Completed By | Craig Towart
SECTION 2: Introduction
Carry out 6 Monthly Mechanical Check

## Report
ZENITH MECHANICAL SERVICES
Report Number | 24-41860
SECTION 3: Report
Ct 25/1/24 3x Hamworthy fleet f125v 1=operational 2=operational 3=operational 2x Hamworthy powerstock calorifiers both operational 1x Hamworthy chesil pressuration unit operational no overflow connected to run to drain ( 1x3m 1 1/4 white solvent pipe 3x 1 1/4 90 1 x 1 1/4 45 2 x rubber lined 1 1/4 clips ) 1x c/h expansion vessel set at 1.5 bar 2 dhw expansion vessel set at 3 bar Primary dhw pumps 2x Grundfos Magna 3 40-120 1= operational amps 0.19 2= operational amps 0.15 Dhw secondary return 1x Grundfos Magna 3 25-60 operational amps 0.1 Heating pumps 2x Grundfos Magna 3 40-150 1=operational amps 1.0 2= operational amps 0.8 Vt valve Schneider m700 operational 2x Schneider 3 way valves operational Gauges and sensors operational Valves operational 8x prv operational 1x interlock operational Water sample took awaiting results Lagging good Flue good Pipework good expect for leak on cold water inlet to cal 1 which will require drain down and pipe work alteration to re correct ( 28 male ion 2x28mm crimp t 2x 28-22mm reducer crimp 22mm drain off 1m 28mm copper)

## Photos
ZENITH MECHANICAL SERVICES
Report Number | 24-41860
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 24-41860
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 24-41860
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 24-41860
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 24-41860
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes