## Cover
ZENITH MECHANICAL SERVICES
Plumbing & Gas Services
82 Viewpoint Business Centre, Consett, County Durham, DH8 6BN
Contact Number: 01207 693 849
Email: admin@zenithmechanical.com
REPORT ON
The Elms ( Communal Area )
Chester Le Street
County Durham
DH2 3EJ
CARRIED OUT ON BEHALF OF
Karbon Homes
REPORT NUMBER: 24-43351
DATE OF REPORT: 11/06/2024
Registered in England Company No. 923602
Directors: Josh Hodgson and David Hunter |  | Gas Safe registration number: 527432

## Contents
ZENITH MECHANICAL SERVICES
Report Number | 24-43351
Contents of Report
Section 1 | Job information
Section 2 | Introduction
Section 3 | Report
Section 4 | Photographs
SECTION 1: Job Information
Client | Karbon Homes
Address | Number Five
Gosforth Park Avenue
Gosforth Business Park
Newcastle upon Tyne
NE12 8EG
Site Address | The Elms ( Communal Area )
Chester Le Street
County Durham
DH2 3EJ
Carried Out On | 27/02/2024, 17/04/2024
Survey Completed By | Graham Parker
SECTION 2: Introduction
Commercial Boiler Repairs - several properties no heating 20, 3, 24, 2 x guest rooms - also still issues with hot water at flat 34.

## Report
ZENITH MECHANICAL SERVICES
Report Number | 24-43351
SECTION 3: Report
Checked a few properties to diagnose what the issue was. Found the circulating pipe work not to be up to temperature. Found in the plant room that only the CHP and 1 boiler was only operating and found that the problem lies with the BMS as this is not bringing on the boilers even though there is a demand the boiler temperature was only at 65 degrees. I have put the boilers in to manual and found this solved the water temperature issue within the flats. Multiphase is required to visit to find the issue within the BMS. NH 15/04/2024 - MultiPhase attended 05/03/2024 "Attended site to investigate issue with boilers not staging/enabling correctly. Upon inspection found boilers 2, 3 & 5 not firing when the 10v enable signal was being sent. Suspect faulty 0-10V boiler PCB's. Heating engineers required to investigate. Also found Universal outputs 5 & 6 on Mod 4 not giving out 10v to boilers 2 & 3 when display is showing as enabled. Suspect module has failed. Return required to check software correlates to outputs showing on the display. If this is the case, a new module will be required. Software backup is required to be able to check installed strategy. Left boilers 2 & 3 enable cables piggy backed into functioning 10V outputs in BMS panel for heating engineer testing purposes. Boilers 2, 3 & 5 left in hand set at 70*c until faults are fixed. 17/04/24 GP All apartment numbers operational

## Photos
ZENITH MECHANICAL SERVICES
Report Number | 24-43351
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 24-43351
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 24-43351
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 24-43351
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 24-43351
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes