## Cover
ZENITH MECHANICAL SERVICES
Plumbing & Gas Services
82 Viewpoint Business Centre, Consett, County Durham, DH8 6BN
Contact Number: 01207 693 849
Email: admin@zenithmechanical.com
REPORT ON
Crossgates
Bellshill Close
Hadrian Park
NE28 9TY
CARRIED OUT ON BEHALF OF
S4NT
REPORT NUMBER: 24-46144
DATE OF REPORT: 23/04/2024
Registered in England Company No. 923602
Directors: Josh Hodgson and David Hunter |  | Gas Safe registration number: 527432

## Contents
ZENITH MECHANICAL SERVICES
Report Number | 24-46144
Contents of Report
Section 1 | Job information
Section 2 | Introduction
Section 3 | Report
Section 4 | Photographs
SECTION 1: Job Information
Client | S4NT
Address | Quadrant The Silverlink North
Colbalt Business Park
North Tyneside
NE27 0BY
Site Address | Crossgates
Bellshill Close
Hadrian Park
NE28 9TY
Carried Out On | 23/04/2024
Survey Completed By | Craig Towart
SECTION 2: Introduction
Carry out 6 Monthly Mechanical Check in Plant Room.

## Report
ZENITH MECHANICAL SERVICES
Report Number | 24-46144
SECTION 3: Report
Ppm cross gates 3x hamworthy fleet F85v 1= operational 2= E132 fault and has writing on case saying lmv/ pcb removed not in use 3= isolated and drained due to burst heat exchanger 2lochinvar eco shield water heaters 1= operational 2= operational 2x wilo comfort p235 press uni 1= operational 2= operational Interlock operational Gauges all but one look to be working 4 bar pressure gage required for replacement Valves operational Lagging good Heating section 1 2x Grundfos Magna 3D 65-150F 1= operation Amps 0.26 2= operational amps 0.23 Heating pumps section 2 2x grundfos Magna 3D 40-100f 1= operational amps 0.41 2= operational amps 0.32 Hot water return pump Grundfos ups15-50n operational amps 0.2 Ashp pumos 2x Grundfos mce 80a 1= operational amber circle amps 2.09 2= operational amber circle amps 2.12 Ashp secondary pumos 2x Grundfos mce 90sc 1= operational but amber circle not green tried resetting no joy. Amps 2.4 2= operational amps 2.5 1x Schneider m700 vt head operational 1x v311t valve operation 1x Schneider m700 vt head operational 1x Schneider v321 valve operational 1x heating expansion vessel 1 x Ashp expansion vessel 2 x potable expansion vessel 1= 3bar 22mm compression lockable isolation valve required along with 22 1/2 center tee long stem drain off for future checks. 2= 3 bar no drain off on pipework to drain to take expansion reading isolation valve not closing properly. Requires 1x 22mm lockable isolation compression 1 x 22 1/2 center tee long stem drain off for easier future work as having try catch water in buckets. Ashp expansion vessel 1.5 bar Flue ok Water sample took Recommendations after vist fit drain offs and new isolation valves on both dhw expansion units. Repalce 4 bar pressure gauge. Repair 2x boilers both potentially leaking heat exchangers and a gas pressure sensor also on boiler 2 however will require gas engineer to confirm.

## Photos
ZENITH MECHANICAL SERVICES
Report Number | 24-46144
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 24-46144
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 24-46144
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 24-46144
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 24-46144
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes