## Cover
ZENITH MECHANICAL SERVICES
Plumbing & Gas Services
82 Viewpoint Business Centre, Consett, County Durham, DH8 6BN
Contact Number: 01207 693 849
Email: admin@zenithmechanical.com
REPORT ON
Rothley Grange ( Flat 23 )
Solway Avenue
Cullercoats
NE330 3AU
CARRIED OUT ON BEHALF OF
S4NT
REPORT NUMBER: 24-46550
DATE OF REPORT: 18/06/2024
Registered in England Company No. 923602
Directors: Josh Hodgson and David Hunter |  | Gas Safe registration number: 527432

## Contents
ZENITH MECHANICAL SERVICES
Report Number | 24-46550
Contents of Report
Section 1 | Job information
Section 2 | Introduction
Section 3 | Report
Section 4 | Photographs
SECTION 1: Job Information
Client | S4NT
Address | Quadrant The Silverlink North
Colbalt Business Park
North Tyneside
NE27 0BY
Site Address | Rothley Grange ( Flat 23 )
Solway Avenue
Cullercoats
NE330 3AU
Carried Out On | 29/04/2024, 10/05/2024, , 16/05/2024
Survey Completed By | Graham Parker
SECTION 2: Introduction
No hot water in the kitchen and the bathroom is intermittent

## Report
ZENITH MECHANICAL SERVICES
Report Number | 24-46550
SECTION 3: Report
Problem is effecting 1 whole wing of 14 flats but the last 4 apartments are the worse. All properties had cold water isolated but problems still exist. Checked the secondary hot water pump and this is not performing to how it should be. So a new replacement is required and this should solve the issue GRUNDFOS UPS 25-80N (180) HOT WATER Also fitted a new tap cartridge to the basin in number 23 as this fell abattoir when removed Used from vehicle stock 1 x armitage shanks cartridge 10:05/24 GP Fitted new pump. worked a treat until the severely under sized thermal overload kept tripping. A temporary flex has been fitted to the pump while I order up new switch 16/05/24 GP Fitted new contactor and overload a larger ampage which was supplied via western automation. We now require to inform Morgan sindall that they have to get the bms guys out as I am getting no power from the controller to draw in the contactor. Relay is fine. Also had to over ride wh1 relay as was giving the water heater and open tank circuit

## Photos
ZENITH MECHANICAL SERVICES
Report Number | 24-46550
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 24-46550
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 24-46550
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 24-46550
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 24-46550
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes