## Cover
ZENITH MECHANICAL SERVICES
Plumbing & Gas Services
82 Viewpoint Business Centre, Consett, County Durham, DH8 6BN
Contact Number: 01207 693 849
Email: admin@zenithmechanical.com
REPORT ON
Eldon Court
Clavering Street
Willington Quary
NE28 6SW
CARRIED OUT ON BEHALF OF
S4NT
REPORT NUMBER: 24-47072
DATE OF REPORT: 13/05/2024
Registered in England Company No. 923602
Directors: Josh Hodgson and David Hunter |  | Gas Safe registration number: 527432

## Contents
ZENITH MECHANICAL SERVICES
Report Number | 24-47072
Contents of Report
Section 1 | Job information
Section 2 | Introduction
Section 3 | Report
Section 4 | Photographs
SECTION 1: Job Information
Client | S4NT
Address | Quadrant The Silverlink North
Colbalt Business Park
North Tyneside
NE27 0BY
Site Address | Eldon Court
Clavering Street
Willington Quary
NE28 6SW
Carried Out On | 13/05/2024
Survey Completed By | Craig Towart
SECTION 2: Introduction
Carry out 6 Monthly Mechanical Checks in Plant Room & clean Filters if possible.

## Report
ZENITH MECHANICAL SERVICES
Report Number | 24-47072
SECTION 3: Report
Eldon court 13/5/24 3 x hanworthy fleet f50v 1= operational 2= operational 3= operational 2 x lochinvar eco shield 1= operational 2= operational 2x wilo pressuration units. 1x ch expansions unit set at 1.5 bar 1x Ashp expansion vessel set at 1.5 bar 2x potable expansion vessels both at 3.5 bar 5x 3 bar prv passes 2x 6 bar prv 1 not sealed after testing needs replaced. 3/4 6bar 2x 7 bar temperature release valves operational 1x dhw return pump Grundfos ups 15-50 Heating pumps 2x grundfos Magna 3 d 40-180F 1=operational amps 0.9 2= operational amps 0.5 Ashp primary pumps 2x grunddoss mce 9058 1= operational orange circle not green amps 2.1 2= operation orange circle amps 2.3 recommend total pumps vist to check pump actual working correctly Ashp secondary pump 2x Magna 3d 32-100 F 1= operational amps 0.24 2 = isolated at electrics need to find out why sticker on pump saying new sensor requires reconnnected and tested operational amps 0.11 1x vt valve Schneider operational 1x interlock operational Valves operational Sensors and gauges operational Pipe work and lagging good Flue good Water sample took and sent Recommendation in report above fit new 6 bar prv as passing part ordered. Get graham or total pumps to check correct Ashp primary pumps and to cut in drain off on potable expansion vessels to make easier and less messy when draining to check pressures in future. 2x 22mm lockable lever valve 2x 22-15 center tees 2 x long stemed drain offs required to fit alterations to potable expansion vessels

## Photos
ZENITH MECHANICAL SERVICES
Report Number | 24-47072
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 24-47072
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 24-47072
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 24-47072
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 24-47072
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes