## Cover
ZENITH MECHANICAL SERVICES
Plumbing & Gas Services
82 Viewpoint Business Centre, Consett, County Durham, DH8 6BN
Contact Number: 01207 693 849
Email: admin@zenithmechanical.com
REPORT ON
Eccles Grange
Church Road
Backworth
NE27 0FW
CARRIED OUT ON BEHALF OF
S4NT
REPORT NUMBER: 24-49694
DATE OF REPORT: 31/07/2024
Registered in England Company No. 923602
Directors: Josh Hodgson and David Hunter |  | Gas Safe registration number: 527432

## Contents
ZENITH MECHANICAL SERVICES
Report Number | 24-49694
Contents of Report
Section 1 | Job information
Section 2 | Introduction
Section 3 | Report
Section 4 | Photographs
SECTION 1: Job Information
Client | S4NT
Address | Quadrant The Silverlink North
Colbalt Business Park
North Tyneside
NE27 0BY
Site Address | Eccles Grange
Church Road
Backworth
NE27 0FW
Carried Out On | 31/07/2024
Survey Completed By | Craig Towart
SECTION 2: Introduction
Carry out 6 Monthly Mechanical Checks in Plant Room & clean Filters if possible.

## Report
ZENITH MECHANICAL SERVICES
Report Number | 24-49694
SECTION 3: Report
Eccels ppm 2x hamworthy fleet 250v boiler 1 isolated awaiting new heat exchanger still boiler 2 operational 2x hamworthy ps500 calorifiers Microfil pressuration unit operational 2x wilo stratos-d40/1-12 primary pumps 1= operational amps 1.3 2= operational amps 1.5 2x wilo stratos -d40/1-12 lthw pumps 1= operational amps 0.9 2= operational amps 1.1 1x h/w secondary return pump Grundfos Magna 3 25-80n180 operational amps 0.7 2 x biral de stract pumps 1= operational amps 0.1 2= operational amps 0.1 1x c/h expansion vessel test nipple clogged unable to get pressure reading and feels like full of water 2x dhw expansion vessels both 0 pressure rechargerd to 3.5 kept dropping to 1bar BMS not showing any temperature so can’t tell if sensors are faulty or BMS would suggest BMS with faults 1x interlock operational 1x vt valve Schneider m800 operational 2x 3 port valves operational Schneider m800 Water sample took Valves operational Gauges operational except 1 7x prv operational Recommendations - [1 ] 1 1/4 waste from bottom of flue missing needs repiped. - [2 ] Wire new heat meter that has been fitted and not wired. - [ 3] Disconnect wiring from old heat meter so can remove old heat meter - [ 4] Fit new heat exchanger in boiler 1 - [5 ] Replace temperature gauge on secondary return h/w - [6 ] Recommend BMS vist so can access screen and check functioning correctly - [7 ] Replace 2x dhw expansion vessels - [ 8] Replace c/h expansion vessel

## Photos
ZENITH MECHANICAL SERVICES
Report Number | 24-49694
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 24-49694
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 24-49694
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 24-49694
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 24-49694
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes