## Cover
ZENITH MECHANICAL SERVICES
Plumbing & Gas Services
82 Viewpoint Business Centre, Consett, County Durham, DH8 6BN
Contact Number: 01207 693 849
Email: admin@zenithmechanical.com
REPORT ON
Rosebank Hall
Willington Terrace
Wallsend
NE28 7BT
CARRIED OUT ON BEHALF OF
S4NT
REPORT NUMBER: 24-49695
DATE OF REPORT: 09/07/2024
Registered in England Company No. 923602
Directors: Josh Hodgson and David Hunter |  | Gas Safe registration number: 527432

## Contents
ZENITH MECHANICAL SERVICES
Report Number | 24-49695
Contents of Report
Section 1 | Job information
Section 2 | Introduction
Section 3 | Report
Section 4 | Photographs
SECTION 1: Job Information
Client | S4NT
Address | Quadrant The Silverlink North
Colbalt Business Park
North Tyneside
NE27 0BY
Site Address | Rosebank Hall
Willington Terrace
Wallsend
NE28 7BT
Carried Out On | 09/07/2024
Survey Completed By | Craig Towart
SECTION 2: Introduction
Carry out 6 Monthly Mechanical Checks in Plant Room & clean Filters if possible.

## Report
ZENITH MECHANICAL SERVICES
Report Number | 24-49695
SECTION 3: Report
Rosebank hall ppm 3x remeha Quinta pro 115s 1= operational 2= operational a lot of silicone around case to make a seal potentially requires new case and seal 3= error e14 reset boiler also has some silicone making seal on case may require new case and seals. 2 x calorifiers signs of old leaks nothing actually leaking at present. 1x c/h expansion vessel set at 1.5 bar 2x dhw expansion vessel cal 1 set at 3.5 bar cal 2 full of water 1x flamco pressuration unit Pipe work ok a lot of old leaks dried up. Lagging ok few bits worn. Valves ok few had crustation on 2x Grundfoss mce 90 1= operational amps 3.6 2= operational amps 3.9 2x Grundfoss tpe 1= operational amps 3.2 2= operational amps 3.8 1x Grundfoss Magna 32-100n operational amps 0.4 2x de stract pump Grundfoss comfort both operational amps 0.2 Prv 7 operational 1x 3 port hot water Siemens acvatix skd62 operational 1x vt valve heating Siemens acvatix skd62 Water sample took Gauges not many but operational Sensors / BMS not correct water is at 60• but only 42 on BMS from Sensors. 1x gas interlock operational Recommendations replace expansion vessel that is full of water tried re pressuring no joy blue one connected to cal 2 50l floor standing 1” connection required gas engineer to exam if boiler 2/3 need new case and seals or just new seals. Also recommend BMS service / calibration to check system and sensors are correct as don’t seem right on inspection

## Photos
ZENITH MECHANICAL SERVICES
Report Number | 24-49695
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 24-49695
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 24-49695
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 24-49695
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 24-49695
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes