## Cover
ZENITH MECHANICAL SERVICES
Plumbing & Gas Services
82 Viewpoint Business Centre, Consett, County Durham, DH8 6BN
Contact Number: 01207 693 849
Email: admin@zenithmechanical.com
REPORT ON
The Manors
Adderlane Road
West Wylam
NE42 5ET
CARRIED OUT ON BEHALF OF
Karbon Homes
REPORT NUMBER: 24-49870
DATE OF REPORT: 12/07/2024
Registered in England Company No. 923602
Directors: Josh Hodgson and David Hunter |  | Gas Safe registration number: 527432

## Contents
ZENITH MECHANICAL SERVICES
Report Number | 24-49870
Contents of Report
Section 1 | Job information
Section 2 | Introduction
Section 3 | Report
Section 4 | Photographs
SECTION 1: Job Information
Client | Karbon Homes
Address | Number Five
Gosforth Park Avenue
Gosforth Business Park
Newcastle upon Tyne
NE12 8EG
Site Address | The Manors
Adderlane Road
West Wylam
NE42 5ET
Carried Out On | 10/07/2024, 11/07/2024
Survey Completed By | Craig Towart
SECTION 2: Introduction
Relace the Wilo Twin Head Pump assembly with a modern alternative Grundfos assembly. To also replace both 3 Port Valve Couplings & Actuator Heads. Set up, Test & return to operation.

## Report
ZENITH MECHANICAL SERVICES
Report Number | 24-49870
SECTION 3: Report
Ct 10/7/24 Collected rest of parts from western automation on way to job. Got onto site started stripping and fitting 3 port heads before kitchen got in as needed to turn BMS off which isolated kitchens gas. Managed to get first one in and fitted before second one still needed wired. Stripped down pump set and fitted new pumps once fitted and wired checked for leaks and that everything is working. Then tidied plant room up whilst waiting till 13:30 to be able turn BMS off again. Wired second valve up and checked operating correctly. On return visit both pumps had tripped fuse on inspecting the contractors theses are undersized for. We pumps as max amp is 1 amp and new pumps can run to 1.56 amps. I have wired pump into a plug until contactors can be upgraded. Materials 1x Grundfoss double head pump set Magna 1d 40-60 2 x Siemens sa 561 7m 1.5 3 core flex 1x 3 pin plug Fow Upgrade 2x contactors with suitable rampage for new pumps email sent with contactors that are currently fitted

## Photos
ZENITH MECHANICAL SERVICES
Report Number | 24-49870
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 24-49870
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 24-49870
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 24-49870
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 24-49870
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes