## Cover
ZENITH MECHANICAL SERVICES
Plumbing & Gas Services
82 Viewpoint Business Centre, Consett, County Durham, DH8 6BN
Contact Number: 01207 693 849
Email: admin@zenithmechanical.com
REPORT ON
Phoenix Rise
Ambassadors Way
North Shields
NE29 8SQ
CARRIED OUT ON BEHALF OF
S4NT
REPORT NUMBER: 24-52250
DATE OF REPORT: 09/08/2024
Registered in England Company No. 923602
Directors: Josh Hodgson and David Hunter |  | Gas Safe registration number: 527432

## Contents
ZENITH MECHANICAL SERVICES
Report Number | 24-52250
Contents of Report
Section 1 | Job information
Section 2 | Introduction
Section 3 | Report
Section 4 | Photographs
SECTION 1: Job Information
Client | S4NT
Address | Quadrant The Silverlink North
Colbalt Business Park
North Tyneside
NE27 0BY
Site Address | Phoenix Rise
Ambassadors Way
North Shields
NE29 8SQ
Carried Out On | 09/08/2024
Survey Completed By | Craig Towart
SECTION 2: Introduction
Carry out 6 Monthly Mechanical Checks in Plant Room & clean Filters if possible.

## Report
ZENITH MECHANICAL SERVICES
Report Number | 24-52250
SECTION 3: Report
Phoenix rise ppm 3x hamworthy f85v all operational 2x lochinvar eco shields both operational 2x wilo pressuration unit both serviced and reset 1x interlock operational 1x c/h expansion vessel set at 1.5 bar 1x ashp expansion vessll attempted to recharge at 1.5 but didn’t hold 2x hw expansion vesslels no drain off connected manually drained full of water and can’t recharge. Lthw zone 1 pumps 2x Grundfoss Magna 3d 65-150 1= operational amps 0.7 2= operational amps 0.8 Lthw zone 2 pumps 2x Grundfoss Magna 3d 40-150 1= operational amps 0.6 2= operational amps 0.6 Ashp shunt pumps 2x Grundfoss mge 905c 1= operational amps 2.2 2= operational amps 2.4 Ashp 2 x Grundfoss mge 90ld 1= operational amps 3.1 2= operational but amber fault needs app to diagnose l/reset. Amps 2.7 secondary return pump Grundfoss 15/50 n operational amps 0.2 Gauges operational Valves operational sensors operational Lagging ok flue ok 2x vt valves Schneider m700 Water sample taking Prv 8 x tested Recommendations - [ ] Replace Ashp expansion vessel 50l - [ ] Replace 2 x dhw expansion vessels 33l and fit new isolation valves as current ones have failed and fit drain offs. (Will need hot water off to replace) - [ ] Get app and training to diagnose pump fault

## Photos
ZENITH MECHANICAL SERVICES
Report Number | 24-52250
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 24-52250
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 24-52250
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 24-52250
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes
ZENITH MECHANICAL SERVICES
Report Number | 24-52250
SECTION 4: Photos
Room / Area
Description
Notes
Room / Area
Description
Notes
Room / Area
Description
Notes